Ultra-Pure Water Production - Example

-----------------------------------------------------------------------------------------------------

This is a simplified example of a water purification and wastewater treatment plant that is associated with a semiconductor manufacturing facility. It processes 500 m3/h (around 2,200 gpm) of city water and produces 470 m3/h of purified water for use in the fabrication plant. The total solids content of the inlet stream is around 225 ppm.

# Semiconductor Rinse Water Requirements

As line widths characterizing silicon chip circuitry become finer and the electrical resistances required of corresponding devices escalate, specifications for electronic rinse water requirements grow progressively more demanding (Meltzer, 1993). The specifications of high-purify water qualities are often the limits of what is attainable at a given time. They do no necessarily reflect bounds that are sufficient; rather they are the best levels currently possible and thus they must be tolerated. This is what is meant by “state of the art.”  Typical requirements include total organic carbon (TOC) of less than 50 ppb, total salts of less than 20 ppb, resistivity of 18 megohm, etc.

PROCESS DESCRIPTION OF BASE CASE (File UPW_4_5a)

Flowsheet Sections

A flowsheet section is a group of process steps (unit procedures) that have something in common. Flowsheet sections facilitate reporting of results for costing, economic evaluation, and raw material requirements of integrated processes. The flowsheet of this example was divided into four sections: Adsorption, Filtration, Fabrication, and Waste Treatment. The process step icons of the Adsorption, Filtration, Fabrication, and Waste Treatment sections are displayed in blue, green, black, and black, respectively. For information on how to specify flowsheet sections and edit their properties, please consult the Help Facility (search for “sections”).

Adsorption Section

City water (Inlet) is combined with the concentrate (stream S-123) of the RO-101 unit and sent to a granular activated carbon filter (GAC-101) to remove organic compounds (expressed as TOC) and a fraction of the particulate components. Next a cation exchange column is used to remove metal ions (e.g., Na+, K+, Ca+2, Mg+2, etc.). These are represented by the Cation-Hardness and Cation-Other components (see Table 2 for a list of components). The resin is regenerated using a 5.5% wt/wt solution of HCI. The regeneration lasts 45 min operating at a flowrate of 0.06 bed volumes per min or around 800 L/min.

In the purified water stream, the metal ions are substituted by hydrogen ions. The enrichment of the treated water with hydrogen ions (its acidification) converts the bicarbonate and carbonate ions to carbonic acid. The acid decomposes readily to release carbon dioxide.

H++CO3-2HCO3−H++HCO3−H2CO3H2CO3H2O + CO2

Most of the generated CO2 is removed using a vacuum degasifier (DG-101). Next an anion exchange column is used to remove negatively charged ions (e.g., Cl-, NO3-, SO4-2, CO3-2, HCO3-, etc.). For simplicity, these are represented by the Anion-Hardness and Anion-Other components. The column is regenerated using a 4% wt/wt NaOH solution. The regeneration lasts 45 min operating at a flowrate of 0.06 bed volumes per min or around 800 L/min.

Filtration Section

A set of ultrafilter units (UF-101) are used to remove any particulate components and a small fraction of TOC. A recovery of 95% was assumed, which means that 95% of the feed water goes through the membrane. A set of reverse osmosis units (RO-101) are used to remove ionic species and remaining particulate components. A recovery of 95% was assumed for this membrane filtration step. The concentrate of the RO units is recycled back to the beginning of the process.

Note that a single icon (RO-101) represents several RO units operating in parallel. Other sets of identical equipment items, operating in parallel, are represented by single icons as well.  To view the number of equipment items represented by an individual icon, right-click on the icon and select “Equipment Data”.

Fabrication Section

In this section we use two custom mixers to represent the contamination of the purified water in the fabrication plant. The first represents the contamination by sulfuric acid and the second the contamination by nitric acid. The custom mixers offer a convenient way to calculate the flowrate of an added contaminant by specifying its concentration in the outlet stream.

# Waste Water Treatment Section

This part of the process represents the treatment of the wastewater that is generated by the fabrication plant. First, the acidic stream (S-120) is neutralized using a 50% wt/wt solution of Ca(OH)2. The salts that precipitate are removed using a clarifier (CL-101) and further concentrated using a decanter centrifuge (DC-101). The clarified streams (S-130 and S-131) are combined and send to a granular media filter for polishing. The final effluent is discharged into the network of a POTW. The backwash stream (S-133) is sent back to the clarifier.

Table 2 shows the flowrates and compositions of selected streams in the Adsorption and Filtration sections of the flowsheet. S-119 is the feed to the Filtration section, S-121 is the feed to the Fabrication plant, and S-123 is the RO reject that is sent back to the main inlet. The recovery of the overall system is almost 95%. In other words, almost 95% of the feed water is sent to the fabrication plant as purified water. The remaining exits the system as the reject of the UF unit (stream S-112). The total averaged flowrate of the cleaning solutions in these two sections is around 12,500 L/h. More than 99% of that is used for washing and regenerating the two ion exchange columns.

Table 2. Adsorption and Filtration Sections – Information on Selected Streams

| Variable | Units | Inlet | # S-119 | # S-121 | # S-123 |
| --- | --- | --- | --- | --- | --- |
| Anion-Hardness | ppm | 100 | 0.4786 | 0.0094 | 9.3933 |
| Anion-Other | ppm | 10 | 0.0479 | 0.0009 | 0.9393 |
| Cation-Hardness | ppm | 100 | 0.4786 | 0.0094 | 9.3933 |
| Cation-Other | ppm | 10 | 0.0479 | 0.0009 | 0.9393 |
| TOC | ppm | 5 | 0.2497 | 0.0048 | 4.8399 |
| CaCO3 | ppm | 200 | 0.9572 | 0.0188 | 18.7866 |
| Total Flowrate | L/h | 500,000 | 524,816 | 473,646 | 24,929 |

Table 3 displays the flowrates and compositions of selected streams in the Wastewater Treatment section of the flowsheet. S-120 is the feed to the Wastewater Treatment section, S-127 is the neutralized stream, and S-132 is the clarified stream, and Effluent is the treated stream that is sent to a POTW. Around 14,890 kg/h of Ca(OH)2 is used for neutralizing the feed to the wastewater treatment section. The neutralization step generates 13,416 kg/h of CaSO4 (gypsum) and 315 kg/h Ca(NO3) 2. Due to the low solubility of CaSO4 (less than 2 g/L), more than 96% of the formed CaSO4 precipitates and is removed using a clarifier (CL-101). The formed Ca(NO3)2 is highly soluble in water and remains in solution. The amount of sludge (Solid Waste) generated by the decanter centrifuge (DC-101) is around 25,250 kg/h. The final effluent has a total hardness of around 3,890 mg CaCO3 per liter.

Table 3. Wastewater Treatment Section – Information on Selected Streams

| Variable | Units | ### S-120 | # S-127 | # S-132 | # Effluent |
| --- | --- | --- | --- | --- | --- |
| Anion-Hardness | ppm | 0.0092 | 0.0089 | 0.0091 | 0.0091 |
| Anion-Other | ppm | 0.0009 | 0.0009 | 0.0009 | 0.0009 |
| Cation-Hardness | ppm | 0.0092 | 0.0089 | 0.0091 | 0.0091 |
| Cation-Other | ppm | 0.0009 | 0.0009 | 0.0009 | 0.0009 |
| Nitric Acid | ppm | 500 | - | - | - |
| Sulfuric Acid | ppm | 19,990 | - | - | - |
| Ca(NO3)2 | ppm | - | 631.5 | 644.4 | 645.0 |
| CaSO4 | ppm | - | 26,916.4 | 2560.5 | 1,666.4 |
| TOC | ppm | 0.0047 | 0.0046 | 0.0047 | 0.0047 |
| CaCO3 | ppm | 21,198 | 22,519 | 4,550 | 3,890 |
| Total Flowrate | L/h | 483,500 | 498,500 | 475,775 | 475,325 |

PROCESS MODIFICATIONS (File UPW_4_5b)

To minimize the amount of city water as well as the amount of disposed wastewater of the plant, it was decided to evaluate options for recycling most of the treated effluent. Open the UPW_4_5b file to see the modified process. A second RO step (RO-102) was used to remove around 95% of the dissolved solids from the treated effluent.  The permeate of the RO unit (S-135), which is around 85% of the feed, is sent back to the main inlet of the water purification section. For a constant flow to the fabrication plant of 473,500 L/h, the recycling of the treated wastewater reduces the inlet flowrate of city water from 500,000 L/h to 96,000 L/h (80.8% reduction) and the amount of effluent wastewater from 475,350 L/h to 71,280 L/h (85% reduction). The flowrate of the purified water (stream S-121) that is fed to the fabrication plant is maintained constant using a flow controller (procedure P-17).

Besides the requirement for additional RO units, the recycling of wastewater results in a 60% increase in the regeneration frequency of the ion exchange columns. SuperPro was used to evaluate the process modifications from an economic point of view. A summary of the results is shown in Table 4. Key assumptions made for the modeling and economic evaluation include:

- purchasing price of city water = $0.5/m3 for city water;

- average disposal cost of wastewater = $1/m3;

- average disposal cost of sludge = $20/metric ton;

- the entire fixed capital investment was depreciated over a period of ten years;

- the UF membranes that treat purified water have an average flux of 30 L/m2-h and are replaced every 20,000 hours;

- the RO membranes that treat purified water have an average flux of 20 L/m2-h and are replaced every 35,500 hours;

- the RO membranes that treat wastewater effluent have an average flux of 13 L/m2-h and are replaced every 20,000 hours;

- the ion exchange resin is replaced every 20,000 hours;

- the resin unit cost is $1.5/L and $4.5/L for cation and anion resins, respectively;

- the unit cost of RO membranes is $15/m2 (this contributes to the consumables cost);

- the unit cost of UF membranes is $60/m2 (this contributes to the consumables cost);

- the equipment-dependent operating cost includes the depreciation and maintenance of the facility.

Table 4.  Operating cost summary (year 2000 prices).

| Cost Item | Initial Plant ($1000/year) | Modified Plant ($1000/year) |
| --- | --- | --- |
| Raw Materials | 4,581 | 3,226 |
| Equipment | 10,628 | 13,682 |
| Labor | 990 | 1,318 |
| Consumables | 595 | 779 |
| Lab/QC/QA | 148 | 198 |
| Waste Trtm/Disp | 8,071 | 4,899 |
| Utilities | 3,459 | 6,534 |
| Total Oper. Cost | 28,472 | 30,636 |
| Unit Cost ($/m3) | 7.60 | 8.20 |
| Total Capital Investment | $60 million | $77 million |

Recycling reduces the cost of raw materials and waste disposal but results in increased equipment-dependent operating cost. This cost covers the depreciation and maintenance of the facility and goes up by around 29% because of the cost of the second set of RO units (RO-102). The cost of utilities also increases because of the additional power consumed by the RO units (RO-102).

At a first glance, it appears that recycling of wastewater is not an attractive process modification since it increases the unit cost of purified water by 7.9% (from $7.6/m3 to $8.2/m3). This conclusion, however, can be readily reversed with a modest increase (of around 20%) in the unit cost of city water and wastewater disposal.

In addition to potential future financial benefits, the main selling point of wastewater recycling in such a facility is the reduced dependency of the company on supply of city water and the improved public image of the facility in the eyes of the surrounding communities.

REFERENCES

1.	Meltzer, T.H. (1993). “High Purity Water Preparation for the Semiconductor, Pharmaceutical, and Power Industries”, Tall Oaks Publishing, Littleton, Colorado.