# Municipal Waste Water Treatment

Modeling and Retrofit Design of a MWWT Plant

This example focuses on the modeling and retrofit design of a municipal wastewater treatment plant. It consists of three design cases that can be found in the examples\munwater directory . The first, mwwt4_0a, represents a typical activated sludge plant without any process steps for nitrogen removal. The second, mwtw4_0b, represents a modified Ludzack-Ettinger process for nitrogen removal. The third, mwtw4_0c, represents a 4-stage Bardenpho process for nitrogen removal.

BASE CASE - ANALYSIS OF AN EXISTING PLANT

This example (filename mwwt4_0a) models an existing treatment plant designed to handle an average flow of 8 MGD. The following are the actual dimensions of the equipment:

Aeration Basin - 4 tanks each having a volume of 2,500 m3 with a depth of 2 m. The 4 tanks form two pairs operating in sequence. Secondary Clarifier - 4 tanks each having a surface area of 490 m2 with a depth of 4 m. Aerobic Digester - 1 tank of 2,500 m3 with a depth of 2 m.

Sludge Thickener - 2 tanks each having a surface area of 250 m2 with a depth of 4 m.

Belt Filter Press - 1 unit with a belt width of 1.5 m. Note that a single icon on the flowsheet may represent multiple identical units operating in parallel.

The following influent characteristics were assumed: (refer to file mwwt4_0a for properties of the user-defined components):

| Component | User | Concentration | Explanation |
| --- | --- | --- | --- |
|  | Defined | (mg/L) |  |
| DomWaste | Yes | 105 | substrate - organic, soluble, biodegradable material |
| X-vss-h | Yes | 53 | active vss (heterotrophic biomass) |
| X-vss-i | Yes | 51 | inert vss |
| X-vss-n | Yes | 3 | vss for nitrifiers (autotrophic biomass) |
| FSS | Yes | 60 | fixed suspended solids (non-biodegradable) |
| TDS | Yes | 306 | total dissolved solids (non-biodegradable) |
| NO3 | Yes | 2.6 | nitrite/nitrate |
| Ammonia | No | 21 | dissolved NH3/NH4 (not NH3-N) |
| Carbon Dioxide | No | 51 | dissolved CO2 (in the form of HCO3 or H2CO3) |
| Water | No | 999,772 | total water (free and bound) |

Please visit the component registration task (select  Tasks \ Register Components & Mixtures \ Pure Components), to view the physical and environmental properties of the various components. For instance, some of the environmental properties of DomWaste are shown below.

Please note that the above values are displayed when you select the DomWaste component by clicking on its line number (# 3) on the left hand side of the ‘Registered Components’ table and then click on the Properties button. Values for these types of properties are already available in the component database for many components. Whenever you enter a new component, you should visit its Properties dialog box to enter appropriate values for the important properties. Note that these values along with the composition of streams are used to calculate the lumped environmental stream properties (BOD, COD, TKN, TSS, etc.). More information on component and environmental stream properties can be found in the manual (Chapters 3 and 4) and the on-line help facility.

The following stoichiometry and kinetic constants in the aeration basin and aerobic digester were assumed:

a. substrate (DomWaste) degradation (the stoichiometry is on a mass basis)

DomWaste    +    NH3    +    O2    ===>    X-vss-h    +    H2O    +    CO2

1 g                  0.1 g        1.4 g                0.8 g           0.8 g         0.9 g

For those of you who are used to thinking in terms of yield coefficients, the above stoichiometry is equivalent to the following yield coefficient.

Y = 0.8 mg vss / mg DomWaste

and since 1 mg DomWaste is equivalent to 2x0.68 = 1.36 mg BOD5 (see table of environmental component properties), the yield coefficient is also equal to

Y = 0.8/1.36 = 0.588 mg vss / mg BOD5

Note that in Pro-Designer the user never specifies yield coefficients since that information can be extracted from the reaction stoichiometry.

k  =  2.61 mg BOD5 / (mg vss - d)  =  0.109 mg BOD5 / (mg vss - h)  or

k  =  0.08  mg DomWaste / (mg vss - h)  (since 1 mg DomWaste = 1.36 mg BOD5)

The above rate constant is assumed to apply for T = 20 oC. The impact of temperature variations is accounted for by assuming a theta value of 1.04.

Ks = 6.8 mg BOD5 / L = 5 mg DomWaste / L

Note that we express the kinetic constants in terms of DomWaste concentration and not BOD5 because BOD5 is not a component in Pro-Designer but a stream property. We treat BOD5 as a stream property and not as a component because many different components (e.g., DomWaste, NH3, Biomass, etc.) may contribute to BOD5.

b. nitrification (the stoichiometry is on a mass basis)

NH3      +     O2     +     CO2      ===>      X-vss-n      +      H2O      +      NO3

7.5 g            24.6 g        1.8 g                   1 .0 g                7.7 g             25.2 g

In reality a large amount of alkalinity is consumed: 8.64 g HCO3- is converted to H2CO3 per g of ammonia-nitrogen oxidized. Since in this example we do not consider ionic speciation, the above equation simply shows the net carbon (in the form of CO2) utilized for biomass synthesis. The detailed stoichiometry of nitrification equations can be found in the literature (Metcalf & Eddy, 1991, p. 431).

k = 0.790  mg NH3-N / (mg X-vss-n - d) = 0.033  mg NH3-N / (mg X-vvv-n - h) or

k = 0.040 mg NH3 /  (mg X-vss-n - h)

The above rate constant is assumed to apply for T = 20 oC. The impact of temperature variations is accounted for by assuming a theta value of 1.04.

Ks = 1.4 mg NH3 / L

c. biomass decay (mass basis). Note that this applies for both X-vss-a and X-vss-n.

X-vss-a,n     +     O2      ===>      X-vss-i      +     FSS     +     H2O      +      NH3     +     CO2

1.05 g             1.15 g                  0.2 g              0.1 g          0.35 g             0.1 g          1.45 g

kd = 0.06 1/d = 0.002 1/h

The above rate constant is assumed to apply for T = 20 oC. The impact of temperature variations is accounted by assuming a theta value of 1.04.

Note that in Pro-Designer biomass decay is handled through separate reactions. In other words, you never specify a decay coefficient but instead you specify a decay reaction with its own kinetic constants. This is a richer representation compared to the traditional way because it enables the user to distinguish between active and inert biomass

At this point you should spend some time visiting the various unit procedures of the flowsheet (mwwt4_0a) and familiarizing yourself with the way input data are entered into the system. You may visit the input/output dialog window(s) of a unit procedure or stream by either double-clicking on the icon of that object using the left button of the mouse or by clicking once using the right button and selecting Simulation Data.

The table below shows the calculated environmental properties of the effluent stream in comparison with the influent stream. Note that the values of BOD5, COD, TKN, NH3-N, and NO3-N include the contributions of all compounds (soluble as well as suspended).

| Property | Influent | Effluent | Removal |
| --- | --- | --- | --- |
|  | (mg/L) | (mg/L) | % |
| BOD5 | 226.26 | 40.39 | 82.1 |
| COD | 435.25 | 93.83 | 78.4 |
| TSS | 168.01 | 68.98 | 58.9 |
| TDS | 309.08 | 336.85 | NA |
| TKN | 37.60 | 11.26 | 70.0 |
| NH3-N | 17.33 | 4.72 | 72.8 |
| NO3-N | 0.61 | 7.03 | NA |

RETROFIT CASE I - LUDZACK-ETTINGER PROCESS FOR NITROGEN REMOVAL

The table that shows the environmental properties of influent and effluent streams in the base case clearly indicates that a good fraction of TKN and NH3-N is not removed but is instead converted into NO3-N and remains in the effluent stream. To increase the removal of nitrogen, one of the four aeration tanks is operated under anoxic conditions to promote denitrification. The Pro-Designer flowsheet (filename mwwt4_0b) shows the anoxic stage as a separate unit but in reality it is simply a section of the aeration basin operated under anoxic conditions. The following stoichiometry and kinetic constants were assumed for the denitrification reaction (Eckenfelder, 1989, p. 180 and Metcalf & Eddy, 1991, p. 721):

NO3      +     DomWaste       ===>      X-vss-a      +      H2O      +      N2      +      CO2

62.0 g              34.6 g                          7.4 g               42.6 g           13.2 g         33.4 g

k  =  0.02 mg NO3 / (mg vss - h)

The above rate constant is assumed to apply for T = 20 oC. The impact of temperature variations is accounted by assuming a theta value of 1.06.

Ks = 0.44 mg NO3 / L

The table below shows the effluent environmental properties without (base case) and with the anoxic reaction zone.  As expected, the removal of nitrites/nitrates improves considerably.

| Property | Effluent (mg/L) | Effluent (mg/L) |
| --- | --- | --- |
|  | (Base Case) | (Ludzack-Ettinger) |
| BOD5 | 40.39 | 40.43 |
| COD | 93.83 | 100.25 |
| TSS | 68.98 | 68.32 |
| TDS | 336.85 | 318.10 |
| TKN | 11.26 | 12.72 |
| NH3-N | 4.72 | 6.26 |
| NO3-N | 7.03 | 2.72 |

This design case clearly shows how simple changes in operating conditions (without additional capital expenses) can have a positive impact on the performance of a treatment plant.

RETROFIT CASE II - BARDENPHO PROCESS FOR NITROGEN REMOVAL

The Bardenpho process for nitrogen removal was also analyzed as part of this example. The Pro-Designer flowsheet (filename mwwt4_0c) shows the two anoxic and two aerobic stages as separate process units. In reality, all four stages are accommodated by the four initial tanks. More specifically, one of the four tanks (25% of total volume) houses the first anoxic stage, two other tanks (50% of total volume) house the first aerobic stage, 80% of the fourth tank (or 20% of the total volume) houses the second anoxic zone, and the remaining 20% of the fourth tank (or 5% of the total volume) houses the second aerobic stage. The reaction stoichiometries and kinetics were assumed the same as in the previous examples. The results of the three alternatives are shown below.

| Property | Effluent (mg/L) | Effluent (mg/L) | Effluent (mg/L) |
| --- | --- | --- | --- |
|  | (Base Case) | (Ludzack-Ettinger) | (Bardenpho) |
| BOD5 | 40.39 | 40.43 | 40.72 |
| COD | 93.83 | 100.25 | 105.21 |
| TSS | 68.98 | 68.32 | 68.11 |
| TDS | 336.85 | 318.10 | 307.35 |
| TKN | 11.26 | 12.72 | 13.79 |
| NH3-N | 4.72 | 6.26 | 7.34 |
| NO3-N | 7.03 | 2.72 | 0.25 |

The Bardenpho process does a better job in terms of NO3-N removal as well as in terms of overall nitrogen removal. In terms of BOD and TSS removal, its performance is about the same as that of the other two cases.

ECONOMIC EVALUATION OF THE BASE CASE

The table below provides a breakdown of the annual operating cost for the base (file mwwt4_0a). The equipment-dependent cost is the most important item even when depreciation is ignored. Depreciation can be ignored for very old plants or for plants that were built with public funding. The equipment-dependent cost includes the cost of Depreciation, Maintenance, Insurance, Local Taxes, and Factory Expense (see Chapter 7 of the manual for more detailed information). To estimate the labor cost, it was assumed that a total of 5 operators are required to run the plant on a 24 hour basis. The unit labor cost was assumed $18/hour (benefits are accounted separately). Depending on plant location, this cost may require adjustment. The sludge disposal cost was assumed $50/ton. Again this may vary considerably depending on plant location.

|  | Including Depreciation |  |  | Excluding Depreciation |  |
| --- | --- | --- | --- | --- | --- |
| Cost Item | $/Year | % |  | $/Year | % |
| Labor-Dependent | 414,000 | 2.3 |  | 414,000 | 4.3 |
| Equipment-Dependent | 16,836,000 | 93.37 |  | 8,429,000 | 87.57 |
| Laboratory/QC/QA | 62,000 | 0.34 |  | 62,000 | 0.65 |
| Waste Treatment/Disp | 710,000 | 3.93 |  | 710,000 | 7.37 |
| Utilities | 11,000 | 0.06 |  | 11,000 | 0.11 |
| Total | 18,032,000 | 100.000 |  | 8,989,708 | 100.00 |

To eliminate the cost of depreciation, the value of "Portion of Purchase Cost Already Depreciated" for all the equipment items was set to 100%. The above variable is displayed on the Adjustments tab of the Equipment Data dialog of a process step (right click on a process step icon and select Equipment Data...). The material for the above table was extracted from the itemized cost report (ICR) of the base case and the case that excluded depreciation.

If we had to build a plant of this size, the capital investment would be around $93 million.  Other important economic results for this case appear in the table below:

Including Depreciation:

| TOTAL CAPITAL INVESTMENT | 93,018,000 | $ |
| --- | --- | --- |
| OPERATING COST | 18,032,000 | $/year |
| PROCESSING RATE | 14,990,500,800 | kg/year of Influent |
| UNIT PROCESSING COST | 1.203 | $/MT of Influent |
| TOTAL REVENUES | 29,981,000 | $/year |
| GROSS MARGIN | 39.85 | % |
| RETURN ON INVESTMENT | 16.74 | % |
| PAYBACK TIME | 5.97 | years |
| IRR AFTER TAXES | 3.98 | % |

Excluding Depreciation:

| TOTAL CAPITAL INVESTMENT | 93,018,000 | $ |
| --- | --- | --- |
| OPERATING COST | 9,626,000 | $/year |
| PROCESSING RATE | 14,990,500,800 | kg/year of Influent |
| UNIT PROCESSING COST | 0.642 | $/MT of Influent |
| TOTAL REVENUES | 29,981,000 | $/year |
| GROSS MARGIN | 67.89 | % |
| RETURN ON INVESTMENT | 13.13 | % |
| PAYBACK TIME | 7.62 | years |
| IRR AFTER TAXES | 12.11 | % |

The detailed results of the economic evaluation can be viewed by selecting Economic Evaluation Report from the View menu. If you have a demo copy of SuperPro Designer, you may have to generate the report by selecting Tasks\Generate Economic Evaluation Report before you can view it.

Note that several multipliers are used to estimate the capital investment of a treatment plant and perform its cost analysis and economic evaluation.  Please read Chapter 2 of the manual for more information on how to access and modify those multipliers. Note that the current default multipliers in Pro-Designer are more appropriate for chemical manufacturing plants than wastewater treatment plants. Future versions of Pro-Designer will be provided with setting files that will include application-specific multipliers. Presently, you may do something equivalent by creating a template file using your own validated multipliers. The mwwt4_0a file used for this example is a good starting point.

WHERE DO I GO FROM HERE?

The three files created for this example can be used as a good starting point for modeling your own treatment plants. You may add more components and/or unit procedures to this flowsheet in order to better approximate your own processes. For instance, you may add PO4 and introduce reactions that consume and generate PO4 to model phosphorous removal. You may add VOCs to model emissions from treatment plants. You can also add heavy metals and other regulated compounds to track their fate in wastewater treatment facilities.

Warning!  As you increase the number of components, reactions, process steps, and recycle loops, Pro-Designer will take longer to converge.  Consequently, you are strongly advised to increase the complexity of your flowsheets in small steps so that you can be in a position to readily identify the changes that really slow down the convergence. For instance, reactions with very different reaction rates specified in a single unit procedure slow down the calculations considerably and may even cause convergence to fail. In such situations, it may be better to simplify your model by ignoring a slow reaction, at least at the early stages of analysis. Similarly, if you have a very fast reaction, you may model it using a generic reaction box (you specify the stoichiometry and the extent of conversion) and assume 100% conversion.

A New Way of Thinking. The use of Pro-Designer, like most other software tools, requires a new way of thinking. This is particularly important for those of you who have little or no previous experience in process simulation. Remember that with simulation we only attempt to approximate the behavior of the real world. It is impossible to represent 100% the behavior of a treatment plant on the computer. Consequently, your objective should be to limit the analysis to those variables that are of interest to you from a design (if the objective is to design a new plant or retrofit an existing one) or operations (if the goal is to improve the performance of an existing plant) point of view.

We are here to support you. If you have difficulty using Pro-Designer to its full potential, please do not hesitate to contact our tech-support office. Our staff will be happy to assist you and provide you with guidance. Also, it may be a good idea to attend one of our training courses or arrange for a training course at your company's site.

INTELLIGEN, INC.

2326 Morse Avenue

Scotch Plains, NJ 07076

Tel:  (908) 654-0088 or (973) 622-1212

Fax: (908) 654-3866

Email:  TechSupport@intelligen.com

WWW:  http://www.intelligen.com

REFERENCES

W. Wesley Eckenfelder, Jr. (1989), Industrial Water Pollution Control, McGraw-Hill, 2nd Edition.

Metcalf & Eddy, Inc. (revised by G. Tsobanoglous and F.L Burton) (1991), Wastewater Engineering - Treatment, Disposal, and  Reuse, McGraw-Hill, 3rd edition.

Acknowledgment

The above three examples were generated using material initially developed by Drs. J.R.V. Flora and A.S. McAnally in the department of Civil and Environmental Engineering at University of South Carolina as part of a NSF-funded, Gateway Coalition project. The objective of the project was the development of “Modules to Support Environmental Engineering Education” and part of the project involved the evaluation of EnviroPro/SuperPro Designer as a potential educational tool.