Industrial Wastewater Treatment Example

-----------------------------------------------------------------------------------------------------

This design case analyzes an industrial wastewater treatment plant and demonstrates how to track the fate of multiple chemical components (constituents) in an integrated facility.The design case file, iwwt4_0, can be found in the examples\indwater directory.

CHEMICAL COMPONENTS AND CHEMISTRY

The flowrate and composition of the influent stream is shown below:

This corresponds to a relatively small plant with an average throughput of 1 million gallons per day (MGD). Glucose represents the easily biodegradable components while benzene represents the recalcitrant (not easily biodegradable) and volatile components.

Please visit the component registration dialog (select  Tasks \ Register Components & Mixtures \ Pure Components), to view the physical and environmental properties of the various components. Some of the environmental properties of Glucose are shown below.

Please note that the above values are displayed when you select the Glucose component by clicking on its line number (# 5) on the left hand side of the ‘Registered Components’ table and then click on the Properties button. Values for these types of properties are already available in the component database for many components. Whenever you enter a new component, you should visit its Properties dialog box to enter appropriate values for the important properties. Note that these values along with the composition of streams are used to calculate the lumped environmental stream properties (BOD, COD, TKN, TSS, etc.). More information on component and environmental stream properties can be found in the manual (Chapters 3 and 4) and the on-line help facility.

You may view the stoichiometry and kinetics of the various reactions by visiting the reaction dialog windows of the aeration basin (AB-101). The following stoichiometry and kinetic constants in the aeration basin were assumed:

a. main substrate (Glucose) degradation (the stoichiometry is on a mass basis)

Glucose    ===>    Biomass   +    H2O    +    CO2

1 g                      0.4 g             0.3 g           0.3 g

For those of you who are used to thinking in terms of yield coefficients, the above stoichiometry is equivalent to the following yield coefficient.

Y = 0.4 mg Biomass / mg Glucose

Note that in Pro-Designer the user never specifies yield coefficients since that information can be extracted from the reaction stoichiometry.

kmaxo  =  0.08 1/h  at T = 20 deg C

theta = 1.04 (to account for the impact of temperature variations).

Ks = 5 mg Glucose/ L

Note that we express the kinetic constants in terms of Glucose concentration and not BOD5 because BOD5 is not a component in Pro-Designer but a stream property. We treat BOD5 as a stream property and not as a component because many different components (e.g., Glucose, Benzene, etc.) may contribute to BOD5.

b. benzene degradation (the stoichiometry is on a mass basis)

Benzene   ===>    Biomass   +    H2O    +    CO2

1 g                      0.3 g             0.4g           0.3 g

kmaxo  =  0.019 1/h  at T = 20 deg C

theta = 1.04 (to account for the impact of temperature variations).

Ks = 13.571 mg Benzene / L

c. biomass decay

Biomass   ===>    DeadBiomass

1 g                           1 g

k  = 0.005 1/h

Note that in Pro-Designer biomass decay is handled through a separate reaction. In other words, you do not specify a decay coefficient but instead you specify a decay reaction with its own kinetic constants. This is a richer representation compared to the traditional way because it enables the user to distinguish between active and inert biomass

In the above reactions we ignored the consumption of oxygen and nitrogen for the sake of simplicity. If you wish to consider it, simply modify the stochiometry of the reactions and make sure that those components are available in the feed streams of the reactors.

PROCESS DESCRIPTION

The influent stream is combined with the sludge return stream (Sludge Recycle) and is sent to a sequence of two aeration basins (AB-101 and AB-102) for biological oxidation of the organic material.  Each aeration basin operates at an average hydraulic residence time of 6 hours and an average sludge residence time of 17.2 hours.  A surface aeration system is used to maintain a minimum dissolved oxygen (DO) concentration of 2 mg/l.  A clarifier (CL-101) is used to remove the biomass and thicken it to around 1% wt/wt solids content.  The liquid effluent from the clarifier is further treated using a granular media filter (GMF-101) to remove any remaining particulate components.  The withdrawn sludge (S-116) is concentrated to a 15% (wt/wt) solids content using a belt filter press (BF-101).  The removed water, which contains small amounts of biomass and dissolved solids, is sent back to the aeration basin.  The concentrated sludge stream is dewatered to a final solids concentration of 35% (wt/wt) using a sludge dryer (SLD-101).

VOC EMISSIONS

Volatile organic compounds (VOCs) when present in influent streams tend to volatilize from open tanks and end up in the atmosphere. Current US EPA regulations limit VOC emissions from treatment plants to no more than 25 tons per year (Van Durme, 1993). Pro-Designer can be used to predict VOC emissions using models that are accepted by the EPA. For a detailed description of the models, visit the Operations section of the help facility and search for the following unit procedures:

1) Clarification - for a detailed description of models for emissions from quiescent tanks.

2) Aerobic BioOxidation -  for a detailed description of models for emissions from agitated tanks.

In this example, emissions occur from the two aeration basins and the clarifier. Please double-click on the emission streams to see the amount of benzene that is emitted. Around 17.4% of the total incoming benzene is emitted from the first aeration basin. A smaller amount (around 3.14% of the total incoming) is emitted from the second aeration basin and a minute amount (0.095%) is emitted from the clarifier.

FLOWSHEET SECTIONS

The concept of flowsheet sections was introduced as part of release 3.0 to facilitate reporting of results for costing, economic evaluation, and raw material requirements of integrated processes. A flowsheet section is a group of unit procedures that have something in common. For instance, the flowsheet of this example has been divided into two sections: 1) BioOxidation and 2) Sludge Treatment. All the procedures of the Sludge Treatment section are displayed in green. For information on how to specify flowsheet sections and edit their properties, please see Chapter 7.1.

ECONOMIC EVALUATION

The table below provides a breakdown of the annual operating cost. The equipment-dependent cost is the most important item even when depreciation is ignored. Depreciation can be ignored for very old plants or for plants that were built with public funding. The equipment-dependent cost includes the cost of Depreciation, Maintenance, Insurance, Local Taxes, and Factory Expense (see Chapter 7 of the manual for more detailed information). To estimate the labor cost, it was assumed that a total of 5 operators (3 in the BioOxidation section and 2 in the Sludge Treatment section) are required to run the plant on a 24 hour basis. The unit labor cost was assumed to be $18/hour. Depending on plant location, this cost may require adjustment. The sludge disposal cost was assumed to be $50/ton. Again this may vary considerably depending on plant location.

|  | Including Depreciation |  |  | Excluding Depreciation |  |
| --- | --- | --- | --- | --- | --- |
| Cost Item | $/Year | % |  | $/Year | % |
| Raw Materials | 294,000 | 3.74 |  | 294,000 | 6.07 |
| Labor-Dependent | 414,000 | 5.28 |  | 414,000 | 8.56 |
| Equipment-Dependent | 6,005,000 | 76.55 |  | 2,998,000 | 61.96 |
| Laboratory/QC/QA | 62,000 | 0.79 |  | 62,000 | 1.28 |
| Waste Trt/Disp | 1,065,000 | 13.57 |  | 1,065,000 | 22.01 |
| Utilities | 5,000 | 0.07 |  | 5,000 | 0.11 |
| Total | 7,845,000 | 100.000 |  | 4,838,000 | 100.00 |

To eliminate the cost of depreciation, the value of "Portion of Purchase Cost Already Depreciated" for all the equipment items was set to 100%. The above variable is displayed on the Adjustments tab of the Equipment Data dialog of a unit procedure (right click on a procedure icon and select Equipment Data...). The material for the above table was extracted from the itemized cost report (ICR) of the base case and the case that excluded depreciation.

If we had to build a plant of this size, the capital investment would be around $33.4 million.  Other relevant economic results for this case appear below.

Including Depreciation:

| TOTAL CAPITAL INVESTMENT | 33,406,000 | $ |
| --- | --- | --- |
| OPERATING COST | 7,845,000 | $/year |
| PROCESSING RATE | 1,247,389,387 | kg/year of Influent |
| UNIT PROCESSING COST | 6.289 | $/MT of Influent |
| TOTAL REVENUES | 9,979,000 | $/year |
| GROSS MARGIN | 21.38 | % |
| RETURN ON INVESTMENT | 12.84 | % |
| PAYBACK TIME | 7.79 | years |

Excluding Depreciation:

| TOTAL CAPITAL INVESTMENT | 33,406,000 | $ |
| --- | --- | --- |
| OPERATING COST | 4,838,000 | $/year |
| PROCESSING RATE | 1,247,389,387 | kg/year of Influent |
| UNIT PROCESSING COST | 3.878 | $/MT of Influent |
| TOTAL REVENUES | 9,979,000 | $/year |
| GROSS MARGIN | 51.52 | % |
| RETURN ON INVESTMENT | 9.23 | % |
| PAYBACK TIME | 10.83 | years |

The detailed results of the economic evaluation can be viewed by selecting Economic Evaluation Report from the View menu. If you have a demo copy of Pro-Designer, you may have to generate the report by selecting “Tasks \ Generate Economic Evaluation Report” before you can view it.

Note that several multipliers are used to estimate the capital investment of a treatment plant and perform its cost analysis and economic evaluation.  Please read Chapter 2 of the manual for more information on how to access and modify those multipliers. Note that the current default multipliers in Pro-Designer are more appropriate for chemical manufacturing plants than wastewater treatment plants. Future versions of Pro-Designer will be provided with setting files that will include application specific multipliers. Presently, you may do something equivalent by creating a template file using your own validated multipliers. The iwwt4_0 file used for this example is a good starting point.

WHERE DO I GO FROM HERE?

This example can be used as a good starting point for modeling your own treatment plants. You may add more components and/or unit procedures to this flowsheet in order to better approximate your own processes. For instance, you may add O2, NH3, PO4 and introduce appropriate reactions for tracking the consumption and generation of those compounds. The example on municipal wastewater treatment provides information on modeling of nitrogen removal.

Warning!  As you increase the number of components, reactions, process steps, and recycle loops, Pro-Designer will take longer to converge.  Consequently, you are strongly advised to increase the complexity of your flowsheets in small steps so that you can be in a position to readily identify the changes that really slow down the convergence. For instance, reactions with very different reaction rates specified in a single unit procedure slow down the calculations considerably and may even cause convergence to fail. In such situations, it may be better to simplify your model by ignoring a slow reaction, at least at the early stages of analysis. Similarly, if you have a very fast reaction, you may model it using a generic reaction box (you specify the stoichiometry and the extent of conversion) and assume 100% conversion.

A New Way of Thinking. The use of Pro-Designer, like most other software tools, requires a new way of thinking. This is particularly important for those of you who have little or no previous experience in process simulation. Remember that with simulation we only attempt to approximate the behavior of the real world. It is impossible to represent 100% the behavior of a treatment plant on the computer. Consequently, your objective should be to limit the analysis to those variables that are of interest to you from a design (if the objective is to design a new plant or retrofit an existing one) or operations (if the goal is to improve the performance of an existing plant) point of view.

We are here to support you. If you have difficulty using Pro-Designer to its full potential, please do not hesitate to contact our tech-support office. Our staff will be happy to assist you and provide you with guidance. Also, it may be a good idea to attend one of our training courses or arrange for a training course at your company's site.

INTELLIGEN, INC.

2326 Morse Avenue

Scotch Plains, NJ 07076

Tel:  (908) 654-0088 or (973) 622-1212

Fax: (908) 654-3866

Email:  TechSupport@intelligen.com

WWW:  http://www.intelligen.com

REFERENCES

Van Durme, G.P., "Capping Air Emissions from Wastewater," Pollution Engineering, pp. 66-71,  September (1993).